|  |  |  | Windows Server 2016 Converged NIC Step-by-Step |
| --- | --- | --- | --- |
|  |  |  | The Instruction below provide the detailed steps to deploy and diagnose WS2016 Converged NIC using RoCEv2. The Instructions marked in GREEN are for BASIC single adapter scenarios only. This is the case where only the minimal set of operations and resources are desired. The instructions in BLUE are the recommended configuration Datacenter deployment with multiple RDMA Host vNICs for maximum performance and availability. Outline: - Test Basic connectivity - Configure VLAN - Configure QoS - Test RDMA (Mode1 – Native) - Create vSwitch - Configure VLAN - Configure QoS - Test RDMA (Mode2 – Host vNIC) Terminology: - TOR – Top of Rack Switch - vSwitch – Hyper-V Virtual Switch - hNIC – Host vNIC – Virtual NIC from vSwitch - pNIC – Physical NIC – In this example both Physical NICs are named Test-40G-*. |
|  |  |  | 1.0 Test Connectivity |
| 1 |  |  |  |
| 2 |  |  | # First we ensure the pNIC over which we’ll create a vSwitch has basic connectivity to the destination through the Fabric. This encompasses reachability via L3 (i.e., IP level) as well as L2 VLAN. Get-NetAdapter -Name "Test-40G-1" ¦ ft -AutoSize Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- Test-40G-1 Mellanox ConnectX-3 Pro Ethernet Ada... 11 Up E4-1D-2D-07-43-D0 40 Gbps Get-NetIPAddress -InterfaceAlias "Test-40G-1" or Get-NetIPAddress -InterfaceAlias "TEST-40G-1" ¦ Where-Object {$_.AddressFamily -eq "IPv4"} ¦ fl InterfaceAlias,IPAddress . IPAddress : 192.168.1.3 InterfaceIndex : 11 InterfaceAlias : Test-40G-1 AddressFamily : IPv4 Type : Unicast PrefixLength : 24 . . |
| 3 |  |  | # In the case of a Teamed pNIC configuration, also ensure that the other NIC has a valid IP. Note that here we use a separate subnet (xxx.xxx.2.xxx vs xxx.xxx.1.xxx) to facilitate sending from this adapter to the destination. Otherwise, if we place both pNICs on the same subnet the Windows TCPIP stack will load balance among the interfaces, and simple validation becomes more complicated. Get-NetAdapter -Name "Test-40G-2" ¦ ft -AutoSize Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- TEST-40G-2 Mellanox ConnectX-3 Pro Ethernet A...#2 13 Up E4-1D-2D-07-40-70 40 Gbps Get-NetIPAddress -InterfaceAlias "Test-40G-2" or Get-NetIPAddress -InterfaceAlias "Test-40G-2" ¦ Where-Object {$_.AddressFamily -eq "IPv4"} ¦ fl InterfaceAlias,IPAddress . IPAddress : 192.168.2.3 InterfaceIndex : 13 InterfaceAlias : TEST-40G-2 AddressFamily : IPv4 Type : Unicast PrefixLength : 24 . . |
| 4 |  |  | # Ensure bi-directional reachability (ping from source to destination and vice-versa on both systems). The Test-NetConnection command is used, but ping will suffice as well. Test-NetConnection 192.168.1.5 ComputerName : 192.168.1.5 RemoteAddress : 192.168.1.5 InterfaceAlias : Test-40G-1 SourceAddress : 192.168.1.3 PingSucceeded : False PingReplyDetails (RTT) : 0 ms # In some cases, it may be necessary to edit firewall settings. This should be done with security in mind, according to your organizational requirements. In this example, we use the simplistic “disable all” firewall setting. Set-NetFirewallProfile -All -Enabled False Test-NetConnection 192.168.1.5 ComputerName : 192.168.1.5 RemoteAddress : 192.168.1.5 InterfaceAlias : Test-40G-1 SourceAddress : 192.168.1.3 PingSucceeded : True PingReplyDetails (RTT) : 0 ms |
| 5 |  |  | # Repeat the steps above for all subsequent pNICs which will be under the team. Test-NetConnection 192.168.2.5 ComputerName : 192.168.2.5 RemoteAddress : 192.168.2.5 InterfaceAlias : TEST-40G-2 SourceAddress : 192.168.2.3 PingSucceeded : True PingReplyDetails (RTT) : 0 ms |

|  |  |  | 2.0 Configure VLANs |
| --- | --- | --- | --- |
|  |  |  |  |  | Note that in this case the NICs are in ACCESS mode. However when a switch is created later, the VLAN properties are applied at the vSwitch port level. Given a switch will host multiple VLANs, it is necessary for the Physical Switch (ToR) to have it’s port configured in Trunk mode. Consult the switch vendor documentation for instructions. |  |
| 1 |  |  |  |
| 2 |  |  | # Per standards, the QoS Properties in the Physical NIC act on the 802.1p header embedded within the 802.1Q (VLAN) header. Set-NetAdapterAdvancedProperty -Name "Test-40G-1" -RegistryKeyword VlanID -RegistryValue "101" Get-NetAdapterAdvancedProperty -Name "Test-40G-1" ¦ Where-Object {$_.RegistryKeyword -eq "VlanID"} ¦ ft -AutoSize Name DisplayName DisplayValue RegistryKeyword RegistryValue ---- ----------- ------------ --------------- ------------- TEST-40G-1 VLAN ID 101 VlanID {101} # IMPORTANT, Ensure the VLANID takes effect independent of adapter implementation. Restart-NetAdapter -Name "Test-40G-1" # Ensure adapter status is up before proceeding. Get-NetAdapter -Name "Test-40G-1" ¦ ft -AutoSize Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- Test-40G-1 Mellanox ConnectX-3 Pro Ethernet Ada... 11 Up E4-1D-2D-07-43-D0 40 Gbps |
| 3 |  |  | Set-NetAdapterAdvancedProperty -Name "Test-40G-2" -RegistryKeyword VlanID -RegistryValue "102" Get-NetAdapterAdvancedProperty -Name "Test-40G-2" ¦ Where-Object {$_.RegistryKeyword -eq "VlanID"} ¦ ft -AutoSize Name DisplayName DisplayValue RegistryKeyword RegistryValue ---- ----------- ------------ --------------- ------------- TEST-40G-2 VLAN ID 101 VlanID {102} # IMPORTANT, Ensure the VLANID takes effect independent of adapter implementation. Restart-NetAdapter -Name "Test-40G-2" # Ensure adapter status is up before proceeding. Get-NetAdapter -Name "Test-40G-1" ¦ ft -AutoSize Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- Test-40G-2 Mellanox ConnectX-3 Pro Ethernet Ada... 11 Up E4-1D-2D-07-43-D1 40 Gbps |
| 4 |  |  | Note that it may take several seconds for the device to be visible on the network. A Test-NetConnection failure or ping failure _IMMEDIATELY_ after Restart-NetAdapter is not uncommon, simply try again. Reconfirm connectivity after applying the VLAN tag to both adapters. If connectivity breaks, then inspect switch VLAN configuration or destination participation in the same VLAN. Diagnosis: if the VLAN 101 connections work, but the VLAN 102 connections don’t, the problem may be that the switch needs to be configured to allow port traffic on the desired VLAN. You could test check for this by temporarily setting the failing adapters to VLAN 101, and repeating the connectivity test. Test-NetConnection 192.168.1.5 ComputerName : 192.168.1.5 RemoteAddress : 192.168.1.5 InterfaceAlias : Test-40G-1 SourceAddress : 192.168.1.5 PingSucceeded : True PingReplyDetails (RTT) : 0 ms |
| 5 |  |  | # Review instruction in prior step. Test-NetConnection 192.168.2.5 ComputerName : 192.168.2.5 RemoteAddress : 192.168.2.5 InterfaceAlias : TEST-40G-2 SourceAddress : 192.168.2.3 PingSucceeded : True PingReplyDetails (RTT) : 0 ms |

|  |  |  | 3.0 Configure QoS |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  | # Turn on Data Center Bridging (DCB; optional for iWarp in most cases, but necessary at fabric scale such as cross-rack scenarios.) Install-WindowsFeature Data-Center-Bridging Success Restart Needed Exit Code Feature Result ------- -------------- --------- -------------- True No Success {Data Center Bridging} |
| 3 |  |  | # Set the policies for SMB-Direct New-NetQosPolicy "SMB" -NetDirectPortMatchCondition 445 -PriorityValue8021Action 3 Name : SMB Owner : Group Policy (Machine) NetworkProfile : All Precedence : 127 JobObject : NetDirectPort : 445 PriorityValue : 3 |
| 4 |  |  | # Set policies for other traffic on the interface New-NetQosPolicy "DEFAULT" -Default -PriorityValue8021Action 0 Name : DEFAULT Owner : Group Policy (Machine) NetworkProfile : All Precedence : 127 Template : Default JobObject : PriorityValue : 0 |
| 5 |  |  | # Turn on Flow Control for SMB Enable-NetQosFlowControl -priority 3 Get-NetQosFlowControl Priority Enabled PolicySet IfIndex IfAlias -------- ------- --------- ------- ------- 0 False Global 1 False Global 2 False Global 3 True Global 4 False Global 5 False Global 6 False Global 7 False Global |
| 6 |  |  | # If traffic classes other than 3 are enabled for FlowControl, make sure flow control is disabled for them. Under more complex configuration, the other traffic classes may require flow control, however said scenarios are outside the scope of this document. Disable-NetQosFlowControl -priority 0,1,2,4,5,6,7 Get-NetQosFlowControl Priority Enabled PolicySet IfIndex IfAlias -------- ------- --------- ------- ------- 0 False Global 1 False Global 2 False Global 3 True Global 4 False Global 5 False Global 6 False Global 7 False Global |
| 7 |  |  | # Turn this on for the target adapter as well as destination adapters. Enable-NetAdapterQos -InterfaceAlias "Test-40G-1" Get-NetAdapterQos -Name "Test-40G-1" Name : TEST-40G-1 Enabled : True Capabilities : Hardware Current -------- ------- MacSecBypass : NotSupported NotSupported DcbxSupport : None None NumTCs(Max/ETS/PFC) : 8/8/8 8/8/8 OperationalTrafficClasses : TC TSA Bandwidth Priorities -- --- --------- ---------- 0 Strict 0-7 OperationalFlowControl : Priority 3 Enabled OperationalClassifications : Protocol Port/Type Priority -------- --------- -------- Default 0 NetDirect 445 3 |
| 8 |  |  | Enable-NetAdapterQos -InterfaceAlias "Test-40G-2" Get-NetAdapterQos -Name "Test-40G-2" Name : TEST-40G-2 Enabled : True Capabilities : Hardware Current -------- ------- MacSecBypass : NotSupported NotSupported DcbxSupport : None None NumTCs(Max/ETS/PFC) : 8/8/8 8/8/8 OperationalTrafficClasses : TC TSA Bandwidth Priorities -- --- --------- ---------- 0 Strict 0-7 OperationalFlowControl : Priority 3 Enabled OperationalClassifications : Protocol Port/Type Priority -------- --------- -------- Default 0 NetDirect 445 3 |
| 9 |  |  | # Give SMB Direct (RDMA) 50% of the bandwidth reservation New-NetQosTrafficClass "SMB" -priority 3 -bandwidthpercentage 50 -algorithm ETS Name Algorithm Bandwidth(%) Priority PolicySet IfIndex IfAlias ---- --------- ------------ -------- --------- ------- ------- SMB ETS 50 3 Global Get-NetQosTrafficClass ¦ ft -AutoSize Name Algorithm Bandwidth(%) Priority PolicySet IfIndex IfAlias ---- --------- ------------ -------- --------- ------- ------- [Default] ETS 50 0-2,4-7 Global SMB ETS 50 3 Global |
| 10 |  |  | OPTIONAL # Create two more traffic classes for tenant IP traffic. Omit the “IP1” and “IP2” creation if not desired. New-NetQosTrafficClass "IP1" -Priority 1 -bandwidthpercentage 10 -algorithm ETS Name Algorithm Bandwidth(%) Priority PolicySet IfIndex IfAlias ---- --------- ------------ -------- --------- ------- ------- IP1 ETS 10 1 Global New-NetQosTrafficClass "IP2" -Priority 2 -bandwidthpercentage 10 -algorithm ETS Name Algorithm Bandwidth(%) Priority PolicySet IfIndex IfAlias ---- --------- ------------ -------- --------- ------- ------- IP2 ETS 10 2 Global Get-NetQosTrafficClass ¦ ft -AutoSize Name Algorithm Bandwidth(%) Priority PolicySet IfIndex IfAlias ---- --------- ------------ -------- --------- ------- ------- [Default] ETS 30 0,4-7 Global SMB ETS 50 3 Global IP1 ETS 10 1 Global IP2 ETS 10 2 Global |

|  |  |  | 4.0 Configure Debugger (Optional) |
| --- | --- | --- | --- |
| 1 |  |  | # Override the Debugger - by default the attached debugger blocks NetQos Set-ItemProperty HKLM:"\SYSTEM\CurrentControlSet\Services\NDIS\Parameters" AllowFlowControlUnderDebugger -type DWORD -Value 1 –Force Get-ItemProperty HKLM:"\SYSTEM\CurrentControlSet\Services\NDIS\Parameters" ¦ ft AllowFlowControlUnderDebugger AllowFlowControlUnderDebugger ----------------------------- 1 |

|  |  |  | 5.0 Test RDMA (Mode 1) |
| --- | --- | --- | --- |
|  |  |  | This steps ensures the fabric is correctly configured prior to creating a vSwitch and transitioning to RDMA (Mode 2). |
| 1 |  |  |  |
| 2 |  |  | Download the DiskSpd.exe utility and extract into C:\TEST\ http://tinyurl.com/z68h3rc Download the Test-RDMA powershell script to C:\TEST\ https://github.com/Microsoft/SDN/blob/master/Diagnostics/Test-Rdma.ps1 |
| 3 |  |  | Get-NetAdapterRdma ¦ ft -AutoSize Name InterfaceDescription Enabled ---- -------------------- ------- TEST-40G-1 Mellanox ConnectX-4 VPI Adapter #2 True TEST-40G-2 Mellanox ConnectX-4 VPI Adapter True |
| 4 |  |  | # Determine the ifIndex value of your target adapter: Get-NetIPConfiguration -InterfaceAlias "TEST*" ¦ ft InterfaceAlias,InterfaceIndex,IPv4Address InterfaceAlias InterfaceIndex IPv4Address -------------- -------------- ----------- TEST-40G-1 14 {192.168.1.3} TEST-40G-2 13 {192.168.2.3} # Pass the ifIndex value to the Test-RDMA.ps1 script, along with the IP address of the remote adapter on the same VLAN: C:\TEST\Test-RDMA.PS1 -IfIndex 14 -IsRoCE $true -RemoteIpAddress 192.168.1.5 -PathToDiskspd C:\TEST\Diskspd-v2.0.17\amd64fre\ VERBOSE: Diskspd.exe found at C:\TEST\Diskspd-v2.0.17\amd64fre\\diskspd.exe VERBOSE: The adapter TEST-40G-1 is a physical adapter VERBOSE: Underlying adapter is RoCE. Checking if QoS/DCB/PFC is configured on each physical adapter(s) VERBOSE: QoS/DCB/PFC configuration is correct. VERBOSE: RDMA configuration is correct. VERBOSE: Checking if remote IP address, 192.168.1.5, is reachable. VERBOSE: Remote IP 192.168.1.5 is reachable. VERBOSE: Disabling RDMA on adapters that are not part of this test. RDMA will be enabled on them later. VERBOSE: Testing RDMA traffic now for. Traffic will be sent in a parallel job. Job details: VERBOSE: 0 RDMA bytes written per second VERBOSE: 0 RDMA bytes sent per second VERBOSE: 662979201 RDMA bytes written per second VERBOSE: 37561021 RDMA bytes sent per second VERBOSE: 1023098948 RDMA bytes written per second VERBOSE: 8901349 RDMA bytes sent per second VERBOSE: Enabling RDMA on adapters that are not part of this test. RDMA was disabled on them prior to sending RDMA traffic. VERBOSE: RDMA traffic test SUCCESSFUL: RDMA traffic was sent to 192.168.1.5 Note that if the RDMA traffic fails, for the RoCE case specifically, consult your TOR (Physical Switch) configuration for proper PFC/ETS settings which match the Host side settings. Refer to the QoS section in this document for reference values. |
| 5 |  |  | # Determine the ifIndex value of your target adapter: Get-NetIPConfiguration -InterfaceAlias "TEST*" ¦ ft InterfaceAlias,InterfaceIndex,IPv4Address InterfaceAlias InterfaceIndex IPv4Address -------------- -------------- ----------- TEST-40G-1 14 {192.168.1.3} TEST-40G-2 13 {192.168.2.3} # See index v C:\TEST\Test-RDMA.PS1 -IfIndex 13 -IsRoCE $true -RemoteIpAddress 192.168.2.5 -PathToDiskspd C:\TEST\Diskspd-v2.0.17\amd64fre\ VERBOSE: Diskspd.exe found at C:\TEST\Diskspd-v2.0.17\amd64fre\\diskspd.exe VERBOSE: The adapter TEST-40G-2 is a physical adapter VERBOSE: Underlying adapter is RoCE. Checking if QoS/DCB/PFC is configured on each physical adapter(s) VERBOSE: QoS/DCB/PFC configuration is correct. VERBOSE: RDMA configuration is correct. VERBOSE: Checking if remote IP address, 192.168.2.5, is reachable. VERBOSE: Remote IP 192.168.2.5 is reachable. VERBOSE: Disabling RDMA on adapters that are not part of this test. RDMA will be enabled on them later. VERBOSE: Testing RDMA traffic now for. Traffic will be sent in a parallel job. Job details: VERBOSE: 0 RDMA bytes written per second VERBOSE: 0 RDMA bytes sent per second VERBOSE: 541185606 RDMA bytes written per second VERBOSE: 34821478 RDMA bytes sent per second VERBOSE: 954717307 RDMA bytes written per second VERBOSE: 35040816 RDMA bytes sent per second VERBOSE: Enabling RDMA on adapters that are not part of this test. RDMA was disabled on them prior to sending RDMA traffic. VERBOSE: RDMA traffic test SUCCESSFUL: RDMA traffic was sent to 192.168.2.5 |

|  |  |  | 6.0 vSwitch Creation |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  | # Create a simple virtual switch over RDMA capable adapter New-VMSwitch -Name VMSTEST -NetAdapterName "Test-40G-1" -AllowManagementOS $true Name SwitchType NetAdapterInterfaceDescription ---- ---------- ------------------------------ VMSTEST External Mellanox ConnectX-3 Pro Ethernet Adapter |
| 3 |  |  | # AllowManagementOS will create a Host vNIC which inherits the MAC and IP of the Physical NIC under the vSwitch Get-NetAdapter ¦ ft -AutoSize Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- vEthernet (VMSTEST) Hyper-V Virtual Ethernet Adapter #2 27 Up E4-1D-2D-07-40-71 40 Gbps # A Host vNIC is managed two ways, one representation is the NetAdapter view which operates on the "vEthernet (VMSTEST)" Name # The other mechanism is the VMNetworkAdapter view which drops the "vEthernet" prefix and simply uses the vmswitch name. # The VMNetworkAdapter view which allows for setting some properties not accessible via NetAdapter. Get-VMNetworkAdapter –ManagementOS ¦ ft -AutoSize Name IsManagementOs VMName SwitchName MacAddress Status IPAddresses ---- -------------- ------ ---------- ---------- ------ ----------- CORP-External-Switch True CORP-External-Switch 001B785768AA {Ok} VMSTEST True VMSTEST E41D2D074071 {Ok} # Remove the ACCESS VLAN Setting from the physical NIC to prevent it from both auto-tagging the egress traffic with incorrect VLAN ID and filtering ingress traffic which doesn’t match the ACCESS VLAN ID. Set-NetAdapterAdvancedProperty -Name "Test-40G-1" -RegistryKeyword VlanID -RegistryValue "0" # Confirm the VlanID setting: Get-NetAdapterAdvancedProperty -Name 'TEST-10G-1' ¦ Where-Object {$_.RegistryKeyword -eq 'VlanID'} ¦ ft -AutoSize Name DisplayName DisplayValue RegistryKeyword RegistryValue ---- ----------- ------------ --------------- ------------- TEST-10G-1 VLAN ID 0 VlanID {0} |
| 4 |  |  | # When we test the Connection again, it will fail. This is because the physical NIC was placed on an Access VLAN in earlier steps, and when a vSwitch is created on the NIC, the Host vNIC does not inherit the VLAN properties. Test-NetConnection 192.168.1.5 WARNING: Ping to 192.168.1.5 failed -- Status: DestinationHostUnreachable ComputerName : 192.168.1.5 RemoteAddress : 192.168.1.5 InterfaceAlias : vEthernet (CORP-External-Switch) SourceAddress : 10.199.48.170 PingSucceeded : False PingReplyDetails (RTT) : 0 ms Set-VMNetworkAdapterVlan -VMNetworkAdapterName "VMSTEST" -VlanId "101" -Access -ManagementOS Get-VMNetworkAdapterVlan -ManagementOS -VMNetworkAdapterName "VMSTEST" VMName VMNetworkAdapterName Mode VlanList ------ -------------------- ---- -------- VMSTEST Access 101 # Recall that the change may take a few seconds to complete before you can ping the other adapter. Test-NetConnection 192.168.1.5 ComputerName : 192.168.1.5 RemoteAddress : 192.168.1.5 InterfaceAlias : vEthernet (VMSTEST) SourceAddress : 192.168.1.3 PingSucceeded : True PingReplyDetails (RTT) : 0 ms |
| 5 |  |  |  |
| 6 |  |  | # Create a vSwitch in Switch Embedded Teaming mode (ie. SET). New-VMSwitch –Name "VMSTEST" –NetAdapterName "TEST-40G-1","TEST-40G-2" -EnableEmbeddedTeaming $true -AllowManagementOS $true Name SwitchType NetAdapterInterfaceDescription ---- ---------- ------------------------------ VMSTEST External Teamed-Interface # List the Physical adapter team in SET Get-VMSwitchTeam -Name "VMSTEST" ¦ fl Name : VMSTEST Id : ad9bb542-dda2-4450-a00e-f96d44bdfbec NetAdapterInterfaceDescription : {Mellanox ConnectX-3 Pro Ethernet Adapter, Mellanox ConnectX-3 Pro Ethernet Adapter #2} TeamingMode : SwitchIndependent LoadBalancingAlgorithm : Dynamic |
| 7 |  |  | # Display the two (2) views of the Host vNIC . Get-NetAdapter Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- vEthernet (VMSTEST) Hyper-V Virtual Ethernet Adapter #2 28 Up E4-1D-2D-07-40-71 80 Gbps Get-VMNetworkAdapter -ManagementOS Name IsManagementOs VMName SwitchName MacAddress Status IPAddresses ---- -------------- ------ ---------- ---------- ------ ----------- VMSTEST True VMSTEST E41D2D074071 {Ok} |
| 8 |  |  | Test-NetConnection 192.168.1.5 #The remote VLAN 101 adapter. WARNING: Ping to 192.168.1.5 failed -- Status: DestinationHostUnreachable ComputerName : 192.168.1.5 RemoteAddress : 192.168.1.5 InterfaceAlias : vEthernet (CORP-External-Switch) SourceAddress : 10.199.48.170 PingSucceeded : False PingReplyDetails (RTT) : 0 ms # Remove the ACCESS VLAN Setting from the physical NIC to prevent it from both auto-tagging the egress traffic with incorrect VLAN ID and filtering ingress traffic which doesn’t match the ACCESS VLAN ID. Set-NetAdapterAdvancedProperty -Name "Test-40G-1" -RegistryKeyword VlanID -RegistryValue "0" Set-NetAdapterAdvancedProperty -Name "Test-40G-2" -RegistryKeyword VlanID -RegistryValue "0" # Now set the VLANID using the vSwitch specific CMDLETs Set-VMNetworkAdapterVlan -VMNetworkAdapterName "VMSTEST" -VlanId "101" -Access -ManagementOS Get-VMNetworkAdapterVlan -ManagementOS -VMNetworkAdapterName "VMSTEST" VMName VMNetworkAdapterName Mode VlanList ------ -------------------- ---- -------- VMSTEST Access 101 Test-NetConnection 192.168.1.5 ComputerName : 192.168.1.5 RemoteAddress : 192.168.1.5 InterfaceAlias : vEthernet (VMSTEST) SourceAddress : 192.168.1.3 PingSucceeded : True PingReplyDetails (RTT) : 0 ms # If ping still fails, confirm that the “vEthernet (VMSTEST)” has the proper IP address set. Get-NetIPAddress -InterfaceAlias "vEthernet (VMSTEST)" # If not set, use the following. New-NetIPAddress -InterfaceAlias "vEthernet (VMSTEST)" -IPAddress 192.168.1.3 -PrefixLength 24 IPAddress : 192.168.1.3 InterfaceIndex : 37 InterfaceAlias : vEthernet (VMSTEST) AddressFamily : IPv4 Type : Unicast PrefixLength : 24 PrefixOrigin : Manual SuffixOrigin : Manual AddressState : Tentative ValidLifetime : Infinite ([TimeSpan]::MaxValue) PreferredLifetime : Infinite ([TimeSpan]::MaxValue) SkipAsSource : False PolicyStore : ActiveStore |
| 9 |  |  | # Now that we’ve verified the NIC has functionality, we rename the Management NIC and later use separate Host vNICs instances for RDMA Rename-VMNetworkAdapter -ManagementOS -Name “VMSTEST” -NewName “MGT” Get-VMNetworkAdapter -ManagementOS Name IsManagementOs VMName SwitchName MacAddress Status IPAddresses ---- -------------- ------ ---------- ---------- ------ ----------- CORP-External-Switch True CORP-External-Switch 001B785768AA {Ok} MGT True VMSTEST E41D2D074071 {Ok} Get-NetAdapter Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- vEthernet (MGT) Hyper-V Virtual Ethernet Adapter #2 28 Up E4-1D-2D-07-40-71 80 Gbps |

|  |  |  | 7.0 Test vSwitch RDMA (Mode 2) |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  | # Set Priority tagging on the Host vNIC to complement the previous VLAN settings. Set-VMNetworkAdapter -ManagementOS -Name "VMSTEST" -IeeePriorityTag on Get-VMNetworkAdapter -ManagementOS -Name "VMSTEST" ¦ fl Name,IeeePriorityTag Name : VMSTEST IeeePriorityTag : On |
| 3 |  |  | Get-NetAdapterRdma -Name "vEthernet (VMSTEST)" Name InterfaceDescription Enabled ---- -------------------- ------- vEthernet (VMSTEST) Hyper-V Virtual Ethernet Adapter #2 False # Now enable RDMA on the Host vNIC Get-NetAdapter Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- vEthernet (VMSTEST) Hyper-V Virtual Ethernet Adapter #2 27 Up E4-1D-2D-07-40-71 40 Gbps Enable-NetAdapterRdma -Name "vEthernet (VMSTEST)" Get-NetAdapterRdma -Name "vEthernet (VMSTEST)" Name InterfaceDescription Enabled ---- -------------------- ------- vEthernet (VMSTEST) Hyper-V Virtual Ethernet Adapter #2 True |
| 4 |  |  | Get-NetAdapter Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- vEthernet (VMSTEST) Hyper-V Virtual Ethernet Adapter #2 27 Up E4-1D-2D-07-40-71 40 Gbps C:\TEST\Test-RDMA.PS1 -IfIndex 27 -IsRoCE $true -RemoteIpAddress 192.168.1.5 -PathToDiskspd C:\TEST\Diskspd-v2.0.17\amd64fre\ VERBOSE: Diskspd.exe found at C:\TEST\Diskspd-v2.0.17\amd64fre\\diskspd.exe VERBOSE: The adapter vEthernet (VMSTEST) is a virtual adapter VERBOSE: Retrieving vSwitch bound to the virtual adapter VERBOSE: Found vSwitch: VMSTEST VERBOSE: Found the following physical adapter(s) bound to vSwitch: TEST-40G-1 VERBOSE: Underlying adapter is RoCE. Checking if QoS/DCB/PFC is configured on each physical adapter(s) VERBOSE: QoS/DCB/PFC configuration is correct. VERBOSE: RDMA configuration is correct. VERBOSE: Checking if remote IP address, 192.168.1.5, is reachable. VERBOSE: Remote IP 192.168.1.5 is reachable. VERBOSE: Disabling RDMA on adapters that are not part of this test. RDMA will be enabled on them later. VERBOSE: Testing RDMA traffic now for. Traffic will be sent in a parallel job. Job details: VERBOSE: 0 RDMA bytes written per second VERBOSE: 0 RDMA bytes sent per second VERBOSE: 0 RDMA bytes written per second VERBOSE: 0 RDMA bytes sent per second VERBOSE: 0 RDMA bytes written per second VERBOSE: 0 RDMA bytes sent per second VERBOSE: 0 RDMA bytes written per second VERBOSE: 9162492 RDMA bytes sent per second VERBOSE: 938797258 RDMA bytes written per second VERBOSE: 34621865 RDMA bytes sent per second VERBOSE: 933572610 RDMA bytes written per second VERBOSE: 35035861 RDMA bytes sent per second VERBOSE: Enabling RDMA on adapters that are not part of this test. RDMA was disabled on them prior to sending RDMA traffic. VERBOSE: RDMA traffic test SUCCESSFUL: RDMA traffic was sent to 192.168.1.5 |
| 5 |  |  |  |
| 6 |  |  | Set-VMNetworkAdapter -ManagementOS -Name "MGT" -IeeePriorityTag on Get-VMNetworkAdapter -ManagementOS -Name "MGT" ¦ fl Name,IeeePriorityTag Name : MGT IeeePriorityTag : On |
| 7 |  |  | # Now create two Host vNIC for RDMA Add-VMNetworkAdapter –SwitchName "VMSTEST" –Name SMB1 –ManagementOS Add-VMNetworkAdapter –SwitchName "VMSTEST" –Name SMB2 –ManagementOS Get-VMNetworkAdapter -ManagementOS Name IsManagementOs VMName SwitchName MacAddress Status IPAddresses ---- -------------- ------ ---------- ---------- ------ ----------- CORP-External-Switch True CORP-External-Switch 001B785768AA {Ok} Mgt True VMSTEST E41D2D074071 {Ok} SMB1 True VMSTEST 00155D30AA00 {Ok} SMB2 True VMSTEST 00155D30AA01 {Ok} |
| 8 |  |  | # Assign an IP address to the SMB Host vNICs. Note that TEST-40G-1 and TEST-40G-2 physical adapters still have ACCESS VLAN of 101 and 102 set. Hence they’ll tag the traffic and ping succeeds. We’ll remove this in later steps. On page 10, we set both pNIC VLAN IDs to zero, then set the VMSTEST vSwitch to VLAN 101. After that, we can still ping the remote VLAN 101 adapter via the MGT vNIC, but we don’t have any VLAN 102 members. “# Remove the ACCESS VLAN Setting from the physical NIC to prevent it from both auto-tagging the egress traffic with incorrect VLAN ID and filtering ingress traffic which doesn’t match the ACCESS VLAN ID. ”. New-NetIPAddress -InterfaceAlias "vEthernet (SMB1)" -IPAddress 192.168.2.111 -PrefixLength 24 IPAddress : 192.168.2.111 InterfaceIndex : 40 InterfaceAlias : vEthernet (SMB1) AddressFamily : IPv4 Type : Unicast PrefixLength : 24 PrefixOrigin : Manual SuffixOrigin : Manual AddressState : Invalid ValidLifetime : Infinite ([TimeSpan]::MaxValue) PreferredLifetime : Infinite ([TimeSpan]::MaxValue) SkipAsSource : False PolicyStore : PersistentStore #Target the remote VLAN 102 adapter. Test-NetConnection 192.168.2.5 ComputerName : 192.168.2.5 RemoteAddress : 192.168.2.5 InterfaceAlias : vEthernet (SMB1) SourceAddress : 192.168.2.111 PingSucceeded : True PingReplyDetails (RTT) : 0 ms New-NetIPAddress -InterfaceAlias "vEthernet (SMB2)" -IPAddress 192.168.2.222 -PrefixLength 24 IPAddress : 192.168.2.222 InterfaceIndex : 44 InterfaceAlias : vEthernet (SMB2) AddressFamily : IPv4 Type : Unicast PrefixLength : 24 PrefixOrigin : Manual SuffixOrigin : Manual AddressState : Invalid ValidLifetime : Infinite ([TimeSpan]::MaxValue) PreferredLifetime : Infinite ([TimeSpan]::MaxValue) SkipAsSource : False PolicyStore : PersistentStore # No need to test connection again since we have reachability already |
| 9 |  |  | # Since we placed the “MGT” Host vNIC on VLAN 101, we’ll place the RDMA Host vNICs on the pre-existing VLAN 102. Set-VMNetworkAdapterVlan -VMNetworkAdapterName "SMB1" -VlanId "102" -Access -ManagementOS Set-VMNetworkAdapterVlan -VMNetworkAdapterName "SMB2" -VlanId "102" -Access -ManagementOS Get-VMNetworkAdapterVlan -ManagementOS VMName VMNetworkAdapterName Mode VlanList ------ -------------------- ---- -------- SMB1 Access 102 Mgt Access 101 SMB2 Access 102 CORP-External-Switch Untagged |
| 10 |  |  | # Inspect the Mapping of SMB1 and SMB2 to the underlying Physical NICs under the vSwitch Team. The association of Host vNIC to Physical NICs is random and subject to rebalancing during creation and destruction. # Here we use an indirect mechanism to check the current association. Note that the MAC address of SMB1 and SMB2 are associated with NIC Team member “TEST-40G-2”. This is not ideal since Test-40G-1 will does not have an associated SMB Host vNIC and will not allow for utilization of RDMA traffic over the link until an SMB Host vNIC is mapped to it. Get-NetAdapterVPort (Preferred) Get-NetAdapterVmqQueue Name QueueID MacAddress VlanID Processor VmFriendlyName ---- ------- ---------- ------ --------- -------------- TEST-40G-1 1 E4-1D-2D-07-40-71 101 0:17 TEST-40G-2 1 00-15-5D-30-AA-00 102 0:17 TEST-40G-2 2 00-15-5D-30-AA-01 102 0:17 Get-VMNetworkAdapter -ManagementOS Name IsManagementOs VMName SwitchName MacAddress Status IPAddresses ---- -------------- ------ ---------- ---------- ------ ----------- CORP-External-Switch True CORP-External-Switch 001B785768AA {Ok} Mgt True VMSTEST E41D2D074071 {Ok} SMB1 True VMSTEST 00155D30AA00 {Ok} SMB2 True VMSTEST 00155D30AA01 {Ok} # Both commands below should return no info since no mapping has been performed. Get-VMNetworkAdapterTeamMapping -ManagementOS -SwitchName VMSTEST -VMNetworkAdapterName SMB1 Get-VMNetworkAdapterTeamMapping -ManagementOS -SwitchName VMSTEST -VMNetworkAdapterName SMB2 # Map SMB1 and SMB2 to separate physical NIC team members – It _MUST_ be done here before proceeding with further configuration steps. Set-VMNetworkAdapterTeamMapping -ManagementOS -SwitchName VMSTEST -VMNetworkAdapterName "SMB1" -PhysicalNetAdapterName "Test-40G-1" Set-VMNetworkAdapterTeamMapping -ManagementOS -SwitchName VMSTEST -VMNetworkAdapterName "SMB2" -PhysicalNetAdapterName "Test-40G-2" Get-VMNetworkAdapterTeamMapping -ManagementOS -SwitchName VMSTEST NetAdapterName : Test-40G-1 NetAdapterDeviceId : {BAA9A00F-A844-4740-AA93-6BD838F8CFBA} ParentAdapter : VMInternalNetworkAdapter, Name = 'SMB1' IsTemplate : False CimSession : CimSession: . ComputerName : 27-3145G0803 IsDeleted : False NetAdapterName : Test-40G-2 NetAdapterDeviceId : {B7AB5BB3-8ACB-444B-8B7E-BC882935EBC8} ParentAdapter : VMInternalNetworkAdapter, Name = 'SMB2' IsTemplate : False CimSession : CimSession: . ComputerName : 27-3145G0803 IsDeleted : False # Indirectly confirm the MAC associations Get-NetAdapterVmqQueue Name QueueID MacAddress VlanID Processor VmFriendlyName ---- ------- ---------- ------ --------- -------------- TEST-40G-1 1 E4-1D-2D-07-40-71 101 0:17 TEST-40G-1 2 00-15-5D-30-AA-00 102 0:17 TEST-40G-2 1 00-15-5D-30-AA-01 102 0:17 |
| 11 |  |  | !!!IMPORTANT!!! – Run commands on remote system # Since both Host vNICs reside on the same subnet _AND_ same VLAN ID (102), then validate the reachability from the remote system. Test-NetConnection 192.168.2.111 ComputerName : 192.168.2.111 RemoteAddress : 192.168.2.111 InterfaceAlias : Test-40G-2 SourceAddress : 192.168.2.5 PingSucceeded : True PingReplyDetails (RTT) : 0 ms Test-NetConnection 192.168.2.222 ComputerName : 192.168.2.222 RemoteAddress : 192.168.2.222 InterfaceAlias : Test-40G-2 SourceAddress : 192.168.2.5 PingSucceeded : True PingReplyDetails (RTT) : 0 ms |
| 12 |  |  | Set-VMNetworkAdapter -ManagementOS -Name "SMB1" -IeeePriorityTag on Set-VMNetworkAdapter -ManagementOS -Name "SMB2" -IeeePriorityTag on Get-VMNetworkAdapter -ManagementOS -Name "SMB*" ¦ fl Name,SwitchName,IeeePriorityTag,Status Name : SMB1 SwitchName : VMSTEST IeeePriorityTag : On Status : {Ok} Name : SMB2 SwitchName : VMSTEST IeeePriorityTag : On Status : {Ok} |
| 13 |  |  | Get-NetAdapterRdma -Name "vEthernet*" ¦ sort Name ¦ ft -AutoSize Name InterfaceDescription Enabled ---- -------------------- ------- vEthernet (SMB2) Hyper-V Virtual Ethernet Adapter #4 False vEthernet (SMB1) Hyper-V Virtual Ethernet Adapter #3 False vEthernet (MGT) Hyper-V Virtual Ethernet Adapter #2 False Enable-NetAdapterRdma -Name "vEthernet (SMB1)" Enable-NetAdapterRdma -Name "vEthernet (SMB2)" Get-NetAdapterRdma -Name "vEthernet*" ¦ sort Name ¦ fl * Name InterfaceDescription Enabled ---- -------------------- ------- vEthernet (SMB2) Hyper-V Virtual Ethernet Adapter #4 True vEthernet (SMB1) Hyper-V Virtual Ethernet Adapter #3 True vEthernet (MGT) Hyper-V Virtual Ethernet Adapter #2 False |
| 14 |  |  | First Run these commands from the remote system. # The intent here is to validate RDMA functionality from the remote system to our system which has a vSwitch, thus testing both adapter under the vSwitch team # Since we placed both Host vNICs (SMB1 and SMB2) on VLAN 102, we need to select the VLAN 102 adapter on the remote system. Here Test-40G-2 does RDMA to SMB1 (192.168.2.111) and SMB2 (192.168.2.222). # Optional: You may need to disable the Firewall on this system. Consult your fabric policy for details. Set-NetFirewallProfile -All -Enabled False Get-NetAdapterAdvancedProperty -Name "Test-40G-2" Name DisplayName DisplayValue RegistryKeyword RegistryValue ---- ----------- ------------ --------------- ------------- . . Test-40G-2 VLAN ID 102 VlanID {102} Get-NetAdapter Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- Test-40G-2 Mellanox ConnectX-3 Pro Ethernet A...#3 3 Up E4-1D-2D-07-43-D1 40 Gbps Get-NetAdapterRdma Name InterfaceDescription Enabled ---- -------------------- ------- Test-40G-2 Mellanox ConnectX-3 Pro Ethernet Adap... True C:\TEST\Test-RDMA.PS1 -IfIndex 3 -IsRoCE $true -RemoteIpAddress 192.168.2.111 -PathToDiskspd C:\TEST\Diskspd-v2.0.17\amd64fre\ VERBOSE: Diskspd.exe found at C:\TEST\Diskspd-v2.0.17\amd64fre\\diskspd.exe VERBOSE: The adapter Test-40G-2 is a physical adapter VERBOSE: Underlying adapter is RoCE. Checking if QoS/DCB/PFC is configured on each physical adapter(s) VERBOSE: QoS/DCB/PFC configuration is correct. VERBOSE: RDMA configuration is correct. VERBOSE: Checking if remote IP address, 192.168.2.111, is reachable. VERBOSE: Remote IP 192.168.2.111 is reachable. VERBOSE: Disabling RDMA on adapters that are not part of this test. RDMA will be enabled on them later. VERBOSE: Testing RDMA traffic now for. Traffic will be sent in a parallel job. Job details: VERBOSE: 34251744 RDMA bytes sent per second VERBOSE: 967346308 RDMA bytes written per second VERBOSE: 35698177 RDMA bytes sent per second VERBOSE: 976601842 RDMA bytes written per second VERBOSE: Enabling RDMA on adapters that are not part of this test. RDMA was disabled on them prior to sending RDMA traffic. VERBOSE: RDMA traffic test SUCCESSFUL: RDMA traffic was sent to 192.168.2.111 C:\TEST\Test-RDMA.PS1 -IfIndex 3 -IsRoCE $true -RemoteIpAddress 192.168.2.222 -PathToDiskspd C:\TEST\Diskspd-v2.0.17\amd64fre\ VERBOSE: Diskspd.exe found at C:\TEST\Diskspd-v2.0.17\amd64fre\\diskspd.exe VERBOSE: The adapter Test-40G-2 is a physical adapter VERBOSE: Underlying adapter is RoCE. Checking if QoS/DCB/PFC is configured on each physical adapter(s) VERBOSE: QoS/DCB/PFC configuration is correct. VERBOSE: RDMA configuration is correct. VERBOSE: Checking if remote IP address, 192.168.2.222, is reachable. VERBOSE: Remote IP 192.168.2.222 is reachable. VERBOSE: Disabling RDMA on adapters that are not part of this test. RDMA will be enabled on them later. VERBOSE: Testing RDMA traffic now for. Traffic will be sent in a parallel job. Job details: VERBOSE: 0 RDMA bytes written per second VERBOSE: 0 RDMA bytes sent per second VERBOSE: 485137693 RDMA bytes written per second VERBOSE: 35200268 RDMA bytes sent per second VERBOSE: 939044611 RDMA bytes written per second VERBOSE: 34880901 RDMA bytes sent per second VERBOSE: Enabling RDMA on adapters that are not part of this test. RDMA was disabled on them prior to sending RDMA traffic. VERBOSE: RDMA traffic test SUCCESSFUL: RDMA traffic was sent to 192.168.2.222 |
| 15 |  |  | # Finally, test for RDMA traffic from the local system to the remote system. Get-NetAdapter ¦ ft –AutoSize Name InterfaceDescription ifIndex Status MacAddress LinkSpeed ---- -------------------- ------- ------ ---------- --------- vEthernet (SMB2) Hyper-V Virtual Ethernet Adapter #4 45 Up 00-15-5D-30-AA-03 80 Gbps vEthernet (SMB1) Hyper-V Virtual Ethernet Adapter #3 41 Up 00-15-5D-30-AA-02 80 Gbps C:\TEST\Test-RDMA.PS1 -IfIndex 41 -IsRoCE $true -RemoteIpAddress 192.168.2.5 -PathToDiskspd C:\TEST\Diskspd-v2.0.17\amd64fre\ VERBOSE: Diskspd.exe found at C:\TEST\Diskspd-v2.0.17\amd64fre\\diskspd.exe VERBOSE: The adapter vEthernet (SMB1) is a virtual adapter VERBOSE: Retrieving vSwitch bound to the virtual adapter VERBOSE: Found vSwitch: VMSTEST VERBOSE: Found the following physical adapter(s) bound to vSwitch: TEST-40G-1, TEST-40G-2 VERBOSE: Underlying adapter is RoCE. Checking if QoS/DCB/PFC is configured on each physical adapter(s) VERBOSE: QoS/DCB/PFC configuration is correct. VERBOSE: RDMA configuration is correct. VERBOSE: Checking if remote IP address, 192.168.2.5, is reachable. VERBOSE: Remote IP 192.168.2.5 is reachable. VERBOSE: Disabling RDMA on adapters that are not part of this test. RDMA will be enabled on them later. VERBOSE: Testing RDMA traffic now for. Traffic will be sent in a parallel job. Job details: VERBOSE: 0 RDMA bytes written per second VERBOSE: 0 RDMA bytes sent per second VERBOSE: 0 RDMA bytes written per second VERBOSE: 15250197 RDMA bytes sent per second VERBOSE: 896320913 RDMA bytes written per second VERBOSE: 33947559 RDMA bytes sent per second VERBOSE: 912160540 RDMA bytes written per second VERBOSE: 34091930 RDMA bytes sent per second VERBOSE: Enabling RDMA on adapters that are not part of this test. RDMA was disabled on them prior to sending RDMA traffic. VERBOSE: RDMA traffic test SUCCESSFUL: RDMA traffic was sent to 192.168.2.5 C:\TEST\Test-RDMA.PS1 -IfIndex 45 -IsRoCE $true -RemoteIpAddress 192.168.2.5 -PathToDiskspd C:\TEST\Diskspd-v2.0.17\amd64fre\ VERBOSE: Diskspd.exe found at C:\TEST\Diskspd-v2.0.17\amd64fre\\diskspd.exe VERBOSE: The adapter vEthernet (SMB2) is a virtual adapter VERBOSE: Retrieving vSwitch bound to the virtual adapter VERBOSE: Found vSwitch: VMSTEST VERBOSE: Found the following physical adapter(s) bound to vSwitch: TEST-40G-1, TEST-40G-2 VERBOSE: Underlying adapter is RoCE. Checking if QoS/DCB/PFC is configured on each physical adapter(s) VERBOSE: QoS/DCB/PFC configuration is correct. VERBOSE: RDMA configuration is correct. VERBOSE: Checking if remote IP address, 192.168.2.5, is reachable. VERBOSE: Remote IP 192.168.2.5 is reachable. VERBOSE: Disabling RDMA on adapters that are not part of this test. RDMA will be enabled on them later. VERBOSE: Testing RDMA traffic now for. Traffic will be sent in a parallel job. Job details: VERBOSE: 0 RDMA bytes written per second VERBOSE: 0 RDMA bytes sent per second VERBOSE: 385169487 RDMA bytes written per second VERBOSE: 33902277 RDMA bytes sent per second VERBOSE: 907354685 RDMA bytes written per second VERBOSE: 33923662 RDMA bytes sent per second VERBOSE: Enabling RDMA on adapters that are not part of this test. RDMA was disabled on them prior to sending RDMA traffic. VERBOSE: RDMA traffic test SUCCESSFUL: RDMA traffic was sent to 192.168.2.5 |

Appendix 1: Physical Switch Configuration

| Arista switch (dcs-7050s-64, EOS-4.13.7M): (These are only commands and their uses; admins need to determine which ports the NICs are connected to. Ensure that VLAN and no-drop policy is set for the priority over which SMB is configured.) | - en (go to admin mode, usually asks for a password) - config (to enter into configuration mode) - show run (shows current running configuration) - find out switch ports to which your NICs are connected to. In these example, they are 14/1,15/1,16/1,17/1. - int eth 14/1,15/1,16/1,17/1 (enter into config mode for these ports) - dcbx mode ieee - priority-flow-control mode on - switchport trunk native vlan 225 - switchport trunk allowed vlan 100-225 - switchport mode trunk - priority-flow-control priority 3 no-drop - qos trust cos - show run (verify that configuration is setup correctly on the ports) - wr (to make the settings persists across switch reboot) Tips: - No #command# negates a command - How to add a new VLAN: int vlan 100 (If storage network is on VLAN 100) - How to check existing VLANs : show vlan - For more information on configuring Arista Switch, search online for: Arista EOS Manual - Use this command to verify PFC settings: show priority-flow-control counters detail |
| --- | --- |
| Dell switch (S4810, FTOS 9.9 (0.0)) | ! dcb enable ! put pfc control on qos class 3 configure dcb-map dcb-smb priority group 0 bandwidth 90 pfc on priority group 1 bandwidth 10 pfc off priority-pgid 1 1 1 0 1 1 1 1 exit ! apply map to ports 0-31 configure interface range ten 0/0-31 dcb-map dcb-smb exit |
| Cisco switch (Nexus 3132, version 6.0(2)U6(1)) | Global: class-map type qos match-all RDMA match cos 3 class-map type queuing RDMA match qos-group 3 policy-map type qos QOS_MARKING class RDMA set qos-group 3 class class-default policy-map type queuing QOS_QUEUEING class type queuing RDMA bandwidth percent 50 class type queuing class-default bandwidth percent 50 class-map type network-qos RDMA match qos-group 3 policy-map type network-qos QOS_NETWORK class type network-qos RDMA mtu 2240 pause no-drop class type network-qos class-default mtu 9216 system qos service-policy type qos input QOS_MARKING service-policy type queuing output QOS_QUEUEING service-policy type network-qos QOS_NETWORK Port specific: switchport mode trunk switchport trunk native vlan 99 switchport trunk allowed vlan 99,2000,2050 çuse VLANs that already exists spanning-tree port type edge flowcontrol receive on (not supported with PFC in Cisco NX-OS) flowcontrol send on (not supported with PFC in Cisco NX-OS) no shutdown priority-flow-control mode on |

Appendix 2: Troubleshooting/Verification steps.

Script to check if RDMA configuration is correct on the host:

https://github.com/Microsoft/SDN/blob/master/Diagnostics/Test-Rdma.ps1

| Cmdlet | Expected | What to do if unexpected is encountered? |
| --- | --- | --- |
| Get-NetAdapterRdma ¦ fl * | Host vNIC and the physical NIC show non-zero RDMA capabilities. | - Make sure the Mlnx miniport and Mlnx bus drivers are latest. For Mellanox, use at least drop 42. - Verify that Mlnx miniport and bus drivers match by checking the driver version through Device Manager. The bus driver can be found in System Devices. The name should start with Mellanox Connect-X 3 PRO VPI. - Make sure Network Direct (RDMA) is enabled on both, physical NIC and host vNIC. - Make sure vSwitch is created over the right physical adapter by checking its RDMA capabilities. - Check EventViewer System log and filter by source “Hyper-V-VmSwitch”. |
|  | - The host vNIC should appear as RDMA capable from SMB’s perspective as well. | - Perform the same steps as above. - Check EventViewer logs for “SMB Client” in Application And Services-> Microsoft-> Windows. |
| Get-NetAdapterQos | Priorities and traffic classes should be displayed as we configured them above in Step 1. vst | - Make sure the physical adapter supports DCB/QoS - Make sure the adapter’s drivers are up to date. |
| Get-SmbMultiChannelConnection | Remote node’s IP address is shown as RDMA capable. | - Make sure ping works both ways. - Make sure firewall is not blocking SMB connection initiation. Specifically, enable the firewall rule for SMB direct port 5445. |
| Get-SmbClientNetworkInterface | Virtual NIC that was enabled for RDMA must be seen as RDMA capable by SMB. | - Make sure ping works both ways. - Make sure firewall is not blocking SMB connection initiation. |
| vstat (Mellanox specific) | RoCE version on both nodes must be the same. This is also a good way to verify that the firmware version on both nodes is latest. | - Set correct RoCE version using Set-MlnxDriverCoreSetting - Install the latest firmware from Mellanox website. |
| Perfmon Counters | Perfmon counters for RDMA should be non-zero |  |

Appendix 3: How to enable Guest RDMA.

How to enable Guest RDMA

- Set the DWORD regkey EnableGuestRdma on the host at KEY_LOCAL_MACHINE\SYSTEM\CurrentControlSet\Services\mlx4_bus\Parameter

While creating registry key name, EnableGuestRdma, make sure there is no space at the end. These types of issues are very hard to figure out.

- Restart the bus driver on the host. It is listed under System Devices:

- Create an IOV enabled vSwitch

  - Non-SET: New-VMSwitch MlnxSwitch -NetAdapterName TEST-40G-1 -EnableIov $true

  - SET:  New-VMSwitch MlnxSetSwitch -NetAdapterName TEST-40G-1,TEST-40G-2 -EnableIov $true

- Currently Guest RDMA is only available on Mellanox port 1. You can find out the port by checking the adapter properties in ncpa.cpl:

- Verify that native and host vNIC RDMA are working according to Converged NIC Configuration and Troubleshooting (vSwitch Host vNIC)

- For a SET vSwitch, make sure you map the vmNic to port 1 of Mellanox NIC by using Set-VMNetworkAdapterTeamMapping

Set-VMNetworkAdapterTeamMapping -VMNetworkAdapterName "Network Adapter" -VMName VM1 -PhysicalNetAdapterName TEST-40G-2

- Get SRIOV working by following the instructions at Enable SR-IOV with Mellanox CX-3

- Make sure that external traffic from the VM flows over SRIOV path by checking Perfmon counters for the VF adapter in the VM.

- Enable guest RDMA inside the VM by doing Enable-NetAdapterRdma on the “Hyper-V Network Adapter”

Check RDMA capabilities of the “Hyper-V Network Adapter” by doing “Get-NetAdapterRdma | fl *”. They should be non-zero.

- Get-SmbClientNetworkInterface should now show Hyper-V Network adapter as RDMA capable.

- Traffic should now flow over RDMA over SRIOV path. Check Perfmon counters for "SMB Direct Connections" inside the VM.

- Guest RDMA can co-exist with host vNIC RDMA but there can be starvation issues because all NDK traffic coming from SMBDirect has ND port 445. So, RDMA traffic from both host vNIC and the VM will be mapped to only one priority and therefore only one traffic class. Following screenshot shows host vNIC RDMA and Guest RDMA on a SET vSwitch working with a remote native RDMA node: